- Scope

- This section describes the requirements for a microwave-type non-contact level gauge.

- The contractor shall supply the non-contact level gauge and accessories as indicated on the plans and as herein specified.

- Products

2.1 Loop-powered Microwave Level Gauge

- Outline

The microwave level gauge shall be a microprocessor-based instrument that uses time of flight principle by radar pulses and providing an electronic output signal proportional to the level of liquid in closed tank or open pit/channel.

It shall consist of a transmitter head and an antenna connected mechanically.

The transmitter head works by loop-powered direct current through 2-wire cable.

The antenna shall be vertically installed into the tank nozzle or on the bracket against surface of liquid. So microwave level gauge measures level without contact with liquid, easy maintenance will be expected. And also it can be installed simply without any special tools or technique.

- Transmitter Head

    - Enclosure shall be IP65 rating of ingress protection.

    - Explosion approval shall be intrinsic safety equivalent to ATEX Ex ia IIC T4.

    - Power supply shall be 16~36V DC in non hazardous area.

In hazardous area, 16~30V DC is required at least.

    - Range of operating temperature shall be -40°C to 70°C (-40°F to 158°F) for transmitter head.

LCD will work within -20°C to 70°C (-4°F to 158°F).

    - Radiating microwave shall have a band frequency as 6GHz or lower and output power as maximum 1 μW.

    - The transmitter head shall provide loop-powered 4-20mA current output with HART® digital communication protocol that interfaces with computer for setup purpose. (Allowable Load Resistance: 360 ohms max. @ 24V DC input)

    - Configuration

The level gauge shall be able to setup by following both methods for service capability.

      - Level gauge configuration data shall be entered via a personal computer with Windows® software utility. (HART® communication modem shall be required.)

      - Key entry shall be available to input the configuration data.

    - Measurements shall be made by time of flight principle by radar pulses.

    - Update cycle of data shall be 1 second at least.

    - Weight of transmitter head shall be approximately 2.5 kg.

- Antenna

- Antenna functions as both radiating and receiving microwave continuously.

- The transducer shall have variety of antenna types and sizes in accordance with measuring range from antenna’s end to 20m (65.62 ft) and size of installing nozzle from DN 50mm to 200mm (2” to 8”) or more.

Ambient temperature of each antenna shall cover -20°C to +150°C (-4°F to +302°F).

      - Cone antenna shall have variety of size of installing nozzle as follows.

          - DN 100mm (4”)

          - DN 150mm (6”)

          - DN 200mm (8”)

Each cone antenna shall be separated from transmitter head in spite of fitting flange that fixes the antenna.

      - Rod antenna for the nozzle size DN 50mm (2”) or more shall have variety of length of inactive part as follows. Inactive part means non-radiation part inside nozzle neck.

          - 100mm (4”) inactive length

          - 250mm (10”) inactive length

- The antennas shall be made by corrosion-inhibiting material, for example Stainless Steel 316L, PFA (fluorine resin) and so on.

- Measuring Performance

- Measuring range : Maximum 20m (65.62 ft) from lower end of antenna

- Measuring accuracy of level shall be as follows.

Measuring range from lower end of antenna  : 0m ~ 0.5m (20”)

± 20mm of reading

Measuring range from lower end of antenna  : 0.5m ~ 20m (65.62 ft)

± 10mm of reading

- Repeatability of level measurement shall be less than ± 1mm.

- Indication

- Display module shall be 5 digits LCD.

- LCD shall alternatively display level, distance, volume, current and amplitude.

- Level units and distance units shall be selectable both meter and feet.

- Functions

The following functions shall be provided:

- Current Output

The level gauge shall alternatively output level, distance, volume and amplitude by 4-20mA current output.

- Signal on alarm

The level gauge shall output alarm by current in accordance with select of alarm type from holding last value, 3.9mA current and 22mA current.

- Volume calculation

The level gauge shall be able to convert measured level to volume for display and current output. The unit of volume is percentage (%) of maximum capacity.

The conversion methods shall cover following types.

          - Spherical tank (typical)

          - Vertical tank (typical)

          - Horizontal cylinder tank (typical)

          - Tank table by linearization points (minimum 20 points)

- Noise treatment

The level gauge shall be able to adjust the threshold level at a part of the measurement range when the gauge incorrectly recognizes and tracks disturbance echo (same as noise) that is in the effective measuring range.

The function shall establish at least 10 points that are coordinated by distance and threshold level values respectively.

- Measured value compensation

The level gauge shall be able to compensate measured value by offset compensation and scale factor (span) compensation.

Also current output shall be able to calibrate by fixed current output.

- Warranty Terms

The manufacturer of the above specified equipment warrants that the equipment shall be free from defects in design or material or workmanship for twelve (12) months after shipment from port/airport.

In the event a component fails to perform as specified or is proven defective in service during the warranty period, the manufacturer shall promptly repair or replace the defective part free of charge.

- Component of

- Minimum components

- Transmitter Head with Cone Antenna (*)			1 unit

or Transmitter Head with Rod Antenna (**)

- Cable Entry Plug (M20x1.5) with blind plug		1 pair

- Site-specific components

- Fitting flange (size referred by nozzle & antenna)		1 piece

- DC power supply Unit (Non-explosion proof)		1 unit

or Barrier type DC power supply unit (Intrinsic Safety)

- HART® communication modem			1 unit

[END]

(*)	: The size of cone antenna shall be specified from 3 sizes.

(**)	: The length of rod antenna shall be specified from 2 lengths.